| Project Name: |  | Date: |  |
| --- | --- | --- | --- |
| Engineer Name: |  | AK P.E. License No.: |  |
| Answers to pertinent questions in this checklist are required for submittals requesting approval of projects constructing new and modifying existing public water systems. Submittals should be in electronic format (Adobe PDF file format is preferred). The approval request should be sent to the dedicated engineering plan submittal email for the regional office covering the particular water system; these email addresses can be found at this link: https://decjnuweb/eh/dw/contact/#eng and the coverage map for our regional offices can be found here: https://decjnuweb/eh/dw/contact/. If the submittal is greater than 15 MB the submitter can use a zipped file or our file transfer website Alaska ZendTo at https://drop.state.ak.us/drop/. We may request hard copies for reviewing certain projects or parts of projects and will contact the submitting engineer, if applicable. Incomplete submittals will not be forwarded to engineering staff for review. Note: When completing this checklist, please answer the questions and also include where in the submittal detailed information is found for each submittal requirement. Please be as specific as possible (specify document name, page number, section number, paragraph, etc.). This will accelerate the review process. |  |  |  |

| Submittal Requirements | Regulatory Reference |
| --- | --- |
| - Cover Letter and Project Report: Does the cover letter state what approval is requested from DEC? Is the engineer’s report sealed, signed, and dated by a Professional Engineer (P.E.) registered in Alaska? Does the engineer’s report include a narrative summarizing the project (where, what, why, when, and how) and describing the basis for design? | 18 AAC 80.200(b) 18 AAC 80.205(a)(4) |
| - Plan Review Fee and Contact Information: A fee will be applied to all plan review requests. A construction approval will not be granted until payment is received. A blank invoice to estimate the fee may be obtained at http://dec.alaska.gov/media/10877/plan-review-invoice.pdf or by contacting DEC. DEC will send an invoice with the correct fee to the applicant prior to payment; therefore, the submittal must include contact information for the person, agency, or company responsible for payment including the following: Name: Mailing address: Telephone number: Email address: | 18 AAC 80.1910 |
| - Project Drawings and Specifications: Are the construction drawings, specifications, and site plan included in the submittal? The construction drawings must be sealed, signed, and dated by an Alaska registered P.E. | 18 AAC 80.205(a)(2) 12 AAC 36.185 |
| - Engineer Submitting Record Drawings: What is the name of and contact information for the Alaska registered P.E. that will be responsible for construction and will sign, date, and seal the record drawings for operational approval? Is the plan for construction inspections sufficient for the engineer to seal the record drawings? What is the contact information for the group or person that will be responsible for commissioning the system? Please note: DEC will not be able to accept blanket disclaimers absolving the engineer sealing the record drawings of all responsibility for the accuracy of drinking water system information in the record drawings. Record drawings are used by DEC to confirm the project, as constructed, meets the requirements of 18 AAC 80, provides public health protection, and meets all written terms and conditions set by the Department for the construction and operation of the project (as applicable). | 18 AAC 80.210(f) |
| - Design Criteria and Calculations: Does the submittal include design criteria, calculations, flow analysis, and other computations (e.g., treatment sizing, disinfection CT, pressure losses, etc.) as appropriate? | 18 AAC 80.205(a)(4) |
| - Operational Narrative: Does the operational narrative for the proposed project include both a description of all unit processes and the operational logic to be followed by the operator or the automated control and alarm systems? | 18 AAC 80.205(b)(9) |
| - Operator Training and Certification: Is documentation included that the system owner or operator is working with the Operator Training and Certification Program (https://dec.alaska.gov/water/operator-certification/), if required, to ensure compliance with 18 AAC 74 after construction of the project? Or, if an existing system, is documentation provided showing there is a certified operator, if required. Note: certified operators are required for any community, non-transient non-community, or surface water system. | 18 AAC 80.007 18 AAC 74 |
| - Manufacturer’s Specifications: Does the submittal include the manufacturer’s specifications for major components of the project and performance curves for the proposed pumps? | 18 AAC 80.205(a)(2) |
| - Backflow and Cross-Connection: Has the engineer included a backflow and cross-connection evaluation? Does it identify high risk service connections such as fire supply systems and medical facilities and describe how backflow prevention will be addressed (e.g., a utility cross-connection program, following UPC standards, etc.)? If the project includes a treatment system, have potential cross-connections been identified and appropriate measures to control them been specified (e.g., backflow prevention assemblies, air gaps, etc.)? Which project specification requires new backflow prevention assemblies to be tested after installation? Will annually testing the assemblies be in the operations and maintenance (O&M) schedule? | 18 AAC 80.025 |
| - Materials in Contact with Drinking Water, NSF/ANSI Standard 61: Is documentation included verifying all components proposed for direct contact with water are certified by an ANSI accredited organization (e.g., NSF International, UL, CSA, WQA, etc.) to NSF/ANSI Standard 61 or an NSF/ANSI standard with equivalent materials health effects evaluation? If there are any components which are not certified in this manner, has the engineer conducted a comprehensive search for a certified alternative? If none exists, how did the engineer justify the proposed non-certified component(s) would be protective of public health? This justification must include the elements listed in 18 AAC 80.030(b)(3). In addition, do the plans specify the design meets the lead content requirements of the Reduction of Lead in Drinking Water Act? Note: if a component is certified to NSF/ANSI Standard 61, the lead content requirement is met for that component. | 18 AAC 80.010(b) 18 AAC 80.030(b) Reduction of Lead in Drinking Water Act (amendment of the Safe Drinking Water Act, Section 1417) 18 AAC 80.205(b)(7) 18 AAC 80.500 |
| - Additives, NSF/ANSI Standard 60: Is documentation included confirming chemical additives (for treatment) and other chemical products (for purposes other than treatment that could leave a residue in the water) proposed for use in the public water system (e.g., disinfectants, coagulants, oxidizing agents, anti-scalants, membrane or UV cleaning chemicals, lubricants, and drilling fluids, etc.) are certified by an ANSI accredited organization (e.g., NSF International, UL, CSA, WQA, etc.) to NSF/ANSI Standard 60 for use in potable water systems? If there are any which are not certified in this manner, what is the engineer’s justification for their use while still being protective of public health? | 18 AAC 80.010(b)(9) 18 AAC 80.30(a) |
| - Master Meter: If the water system is or may be classified as a community or non-transient non-community public water system, and water treatment is or will be provided, how does the project comply with the master water meter requirement? | 18 AAC 80.235 |
| - Operational Control: Which drawing(s) show the location of pressure gages, flow meters, rate of flow controllers, key water sample points (including source “raw” and treated water sample taps), valves, online water quality meters, etc., which assist the operator with operating and monitoring the system in compliance with the requirements of 18 AAC 80? | 18 AAC 80.205(a)(2) 18 AAC 80.205(c)(6) 18 AAC 80.655 |
| - Corrosivity: If the project proposes to make any change to the water source or treatment system, how did the engineer address the potential for these changes to affect the corrosivity of the distributed water in terms of leaching lead and copper and any mitigation that may be necessary? If needed, how does the treatment system design accommodate adding corrosion control treatment in the future (i.e., space for equipment and chemical injection points)? | 18 AAC 80.205(c)(5) |
| - Disinfection before Operation: Which specifications address disinfection of applicable parts of the water system after modification/construction is completed? If an AWWA disinfection standard (i.e., AWWA standards C651 to C654) is not specified, does the proposed method include adequate detail for the contractor to implement? If an AWWA standard is specified, will the contractor have a copy of the standard? How will cross-connection control be accomplished to prevent backflow into the public water system during flushing and disinfecting activities? | 18 AAC 80.205(b)(9) 18 AAC 80.010(d)(2) |
| - Disinfectant Discharge: Has the project been authorized by DEC to discharge the highly chlorinated water used for disinfecting the project components or has it been determined that the water, independent of volume, will meet State water quality standards in 18 AAC 70 and the required effluent limits? Information can be obtained by contacting the regional DEC Wastewater Program Engineering Support and Plan Review staff (contact information at https://dec.alaska.gov/water/wastewater/engineering/area-offices) or visiting DEC Division of Water webpage at https://dec.alaska.gov/water/wastewater/stormwater/permits-approvals/dewater/. | APDES 18 AAC 70 |
| - Project Schedules: Does the cover letter or engineer’s report include a description of the proposed construction and commissioning/start-up schedules including the sequence of construction and transition to operation? | 18 AAC 80.205(b)(9) |
| - Emergency Preparedness: If the submittal involves a new community public water system, is the name and contact information provided for the person that will submit the documentation to satisfy the regulatory emergency preparedness requirements in 18 AAC 80.055 once the system is in operation? Documentation may be required for final approval to operate the system. | 18 AAC 80.055 |
| - New Public Water System-Operation and Maintenance Entity: Has documentation been included showing the existence or formation of a local government organization, a homeowner's association, a private utility, a commercial entity, or other entity to operate and maintain the system? | 18 AAC 80.205(b)(10) |
| - New Public Water System-Sanitary Survey: Will the new public water system owner either have a Water System Inventory Form completed by the engineer responsible for record drawings showing the system has no sanitary deficiencies or a sanitary survey completed by a third-party surveyor? This will be a requirement for obtaining final approval to operate the water system. The Water System Inventory Form may be downloaded from our website at https://dec.alaska.gov/eh/dw/forms/ and information about sanitary surveys and a list of DEC approved surveyors can be found at http://dec.alaska.gov/eh/dw/sanitary-survey/. | 18 AAC 80.430(b) |

Important: See next page for additional submittal requirements for new or newly reclassified community and non-transient non-community public water systems.

Additional submittal requirements for new or newly reclassified community and non-transient non-community public water systems-Capacity Development Review

The Drinking Water Program will use the following information to determine the system’s technical capacity to sustain operations in compliance with federal and state drinking water regulations. Information provided in this checklist will be supplemented by that provided in other relevant engineering plan review checklists, as appropriate, to evaluate the public water system’s (PWS’s) technical capacity. Contact an engineer in a DEC Drinking Water Program office if assistance is needed in determining which other checklists would be applicable. In addition to technical capacity, DEC also needs to determine the managerial and financial capacity of the public water system to have a complete picture of the PWS capacity. The managerial and financial capacity review is conducted by a separate group within DEC, the Capacity Development Program. The Drinking Water Program and the Capacity Development Program will coordinate their efforts when conducting the capacity review, since a construction or operation approval cannot be granted until a PWS can demonstrate it has the technical, managerial, and financial capacity to operate in compliance with the regulations. Refer to 18 AAC 80.207 for further information on what constitutes technical, managerial, and financial capacity and how the Department determines capacity.

| Submittal Requirements | Regulatory Reference |
| --- | --- |
| - Managerial and Financial Capacity: Has the owner of the water system contacted the DEC Capacity Development Program to initiate the managerial and financial capacity review? Contact information can be found at: https://dec.alaska.gov/water/technical-assistance/capacity-development/system-reviews/. | 18 AAC 80.207 |
| Technical Capacity |  |
| - Sufficient Source Water: Attach information showing the source will be able to provide a sufficient quantity of water for the system’s demand. | 18 AAC 80.207(b)(1)(A) |
| - Available Source Water: Attach documentation for each source showing a Water Rights Application has been submitted to the Alaska Department of Natural Resources, thus securing the rights to sufficient source water. | 18 AAC 80.207(b)(1)(A) |
| - O&M Personnel Capability: Attach information showing the ability of system personnel to adequately operate and maintain the system and otherwise apply technical knowledge to the production of water that ensures public health protection (e.g., system-specific training or other equivalent training). | 18 AAC 80.207(b)(2) |
| - O&M Plan: Provide information on the main elements of the operations and maintenance (O&M) manual such as a table of contents or other means to demonstrate what the manual covers. O&M manuals, among other topics, should include start-up and shutdown procedures, routine maintenance of key equipment, calibration and maintenance of water quality monitoring equipment, regulatory record keeping and monitoring requirements, and a troubleshooting section. | 18 AAC 80.207(b)(3)(A) |
| - Other Information: Any other information the applicant believes can help demonstrate technical capacity? | 18 AAC 80.207(b)(3)(C) |