## Jan 2025 ETT
January 2025 ETT List
Note: Column titled "Est. New ETT Score" is the estimated new score based on the violations that have Returned to Compliance (RTCd) during the Quarter. Please note that this score will likely change on the next quarter's list due to further violations being generated. Comments submitted by Drinking Water Program staff on October 31, 2024.
Staff | RMW | Est. New ETT Score | System Information | 10 Point |  |  | 5 Point | [7 empty] | 1 Point | [11 empty] | General Comments | How to Return to Compliance | Known Hardware Problems
|  |  |  | RTCR | SW | Nitrate | RTCR | SW | GWR | Nitrate | Arsenic | DBP | LCR | Rads | RTCR | SW | GWR | Arsenic | DBP | LCR | IOC | VOC | SOC | Rads | CCR | PN
NAKANISHI | YKHC | 66 | ALAKANUK WATER SYSTEM / AK2270362 (570 / C) | [12 empty] | 42 |  |  | 18 | 1 | [6 empty] | Last MOR submitted in April 2024. LT2 sample and TOC from intake last sampled in 2021. Alkalinity and TOC from Treatment plant last sampled in 2016. Last full set of Lead & Copper samples submitted in 2012. | Submit monthly operating report and sample full set of Lead & Copper. Take TOC (intake and treatment plant) and sample for alkalinity. | None known
BJORKMAN | No RMW | 16 | ALPINE INN / AK2244808 (30 / NC) |  |  |  | 1 | [7 empty] | 6 | [11 empty] | System is still closed for the season. | Collect TC samples and submit SSUP in the spring. | None known
LATIMER | DEC | 16 | ANGOON PUBLIC WATER / AK2130017 (450 / C) | [12 empty] | 7 |  |  | 7 | [6 empty] | 1 | On BWN since April 2022. Operator has not completed operator cert testing - recommended hiring a backup or additional operator. Routine sampling is not being completed. Treatment reports are mostly complete and indicate adequate filtration and disinfection. Replacement of mains is scheduled to start in 2025, and the inactive storage tank is expected to be back in service early summer. | Complete all routine sampling, and submit fully complete monthly operator reports on time. Meet operator certification requirements. Submit 2024 CCR and Cert page on time. | One storage tank remains out of service which contributes to lower pressure in part of DS.
SHARP | TCC | 93 | CHALKYITSIK VILLAGE WATER / AK2300183 (76 / C) | [8 empty] | 16 |  |  |  | 4 |  |  | 3 | 1 | [5 empty] | 1 | System began exceeding TTHM LRAA MCL in 4th quarter 2020 and HAA5 MCL in 3rd quarter 2024. System has not collected a routine TCR sample since September 2024 and has not submitted a completed operator report since August 2024 due to operator turn over. System did not collect Lead & Copper sample set during 2024 and has outstanding public notice violations for failure to post TTHM MCL public notice during 2024. | Collect monthly TC with detectable chlorine residual and submit a completed monthly operator report. Collect Lead & Copper sample set between January and June and complete outstanding public notice ASAP. System needs both adequate funding and to optimize or upgrade treatment, including establishing and adhering to a GAC media change out schedule, to help reduce DBP formation. | Adequate GAC change out frequency would reduce chances of DBP exceedance. On 6/20/24 DEC approved plans for a water treatment plant project intended to reduce DBPs. The project includes new winter/summer source intake, replacement WST, and modifications to the WTP, including CT contactor tanks to reduce chlorine use and new type of GAC media. The new WST is in operation, GAC upgrades are not yet.
AGUE | BBAHC | 14 | CHIGNIK BAY WATER SYSTEM / AK2260228 (199 / C) | [12 empty] | 6 |  |  | 6 | 1 | [6 empty] | Last submitted a monthly operator report in February 2024. Last chlorine residual was last recorded w/TC sample in January 2024. System collected annual TTHM sample in the wrong month in 2024. | Submit a complete monthly operator report and record the chlorine residual at the same time and place as the monthly TC sample. Collect a TTHM sample in August 2025. | None known
POEPPEL | YKHC | 11 | CITY OF HOOPER BAY / AK2270312 (1200 / C) | [5 empty] | 1 | [7 empty] | 1 |  | 1 | [7 empty] | Overdue for DBPs. Statewide EPS will continue to reach out to the system about consulting with the state regarding their most recent sanitary survey. | Sample for DBPs between October and December 2025. Consult with the State regarding deficiencies, develop corrective action plan. | None known
DAVIS | BBAHC | 14 | CLARKS POINT WATER SYSTEM / AK2260202 (128 / C) | [5 empty] | 1 | [10 empty] | 5 | [6 empty] | Significant deficiency from 2021 remains unresolved. No 6-month Lead/Copper samples collected since 2017. | Correct sanitary survey deficiency - extend well casing to 12 in. and apply for separation distance waiver. Collect 6-month 10 sample set Lead & Copper. | None known
SHARP | NSHC | 97 | DIOMEDE JOINT UTILITIES / AK2340141 (184 / C) |  |  | 2 |  |  |  |  | 10 |  |  |  |  | 23 | [10 empty] | Diomede exceeds the RAA MCL for Arsenic and Nitrate due to poor source quality. They have not been submitting complete monthly operator reports due to lack of an operator. | System needs to install treatment to address Nitrate, Arsenic, and SWTR. System also needs to hire an operator to complete and submit operator reports. | A new WTP is currently under construction to meet SWTR, nitrate and arsenic MCLs, and corrosion control. A temporary WTP was placed into operation 2024 but did not receive approval because it had not met conditions of operation. Permanent WTP is expected to begin operation summer 2025.
AGUE | YKHC | 16 | EMMONAK WATER SYSTEM / AK2270299 (820 / C) |  |  |  | 1 | [11 empty] | 7 | [7 empty] | Submitted an incomplete Level 1 Assessment. System had TTHM RAA exceedances in 2nd and 3rd quarters of 2023 and the OEL report was not completed. DBP and TOC/Alkalinity samples were last collected in June 2024 and are due quarterly and monthly, respectively. | Complete Level 1 Assessment and OEL Report. Collect DBP and TOC/Alkalinity samples. | None known
MURRAY | No RMW | 20 | FOREST PARK TC / AK2210794 (175 / C) | [5 empty] | 2 | [5 empty] | 2 |  |  |  |  | 1 |  | 1 |  |  | 1 |  | PWS last collected a total coliform sample in July 2024 and VOCs in June 2024. PWS last collected Lead & Copper samples in 2020, last sample due in 2023. Overdue for correcting Survey deficiencies (GWR) from 2016 and 2019 surveys; system reportedly does not have the financial capacity to address the deficiencies. | System must submit engineering plans to correct deficiencies. System must sample for total coliform, VOCs and Lead & Copper. | System has ongoing issues with maintaining pressure.
SHARP | TCC | 13 | GALENA WTP1 - CITY / AK2360272 (490 / C) | [5 empty] | 1 | [17 empty] | System has outstanding sanitary survey deficiencies from their 2023 survey to address. | System must correct outstanding survey deficiencies and submit proof of corrective action. | GAC media in filters has not been replaced in over a year, this affects DBP precursor removal. PWS operators are still adjusting treatment but not using optimized settings suggested by design engineers.
BJORKMAN | DEC | 11 | KAKE MUNICIPAL WATER / AK2130083 (415 / C) | [8 empty] | 2 | [6 empty] | 1 | [7 empty] | System is transitioning operators and starting to get back on track. | Collect a set of DBP samples and complete the OEL. | None known
CAHILL | No RMW | 16 | KING FOR A DAY / AK2299036 (53 / NC) |  |  |  | 2 | [7 empty] | 5 | [11 empty] | PWS did not complete SSUP in 2023 or 2024 seasons. Last TC and Nitrate sample results from 10/01/23. Certified letter sent when PWS moved to monthly TC due to number of violations, but the letter was not picked up. | PWS can return to compliance by taking annual Nitrate and monthly Total Coliform samples. Also needs to complete and return 2025 season SSUP. | None known
BJORKMAN | DEC | 89 | KLAWOCK / AK2120169 (904 / C) | [8 empty] | 17 | [14 empty] | System made repairs to their WST and installed a pax mixer in hopes to decrease the DBP levels. The first set of samples collected are the lowest we have seen in 2024. | Continue to collect DBP samples that allow for the LRAA to fall below the MCL for HAA5. | None known
NAKANISHI | YKHC | 23 | KONGIGANAK WATER SYSTEM / AK2271025 (547 / C) | [12 empty] | 17 |  |  | 3 | [7 empty] | Monthly Operator Reports (MOR) have been insufficient since December 2023, annual DBP's last taken in 2020. | System should provide sufficient MOR and sample for DBP's in 2025. For Significant deficiency, follow-up coordination is underway to establish a corrective action plan timeline. | None known
NAKANISHI | YKHC | 31 | KOTLIK WATER SYSTEM / AK2272004 (617 / C) | [8 empty] | 5 | [7 empty] | 2 | [6 empty] | TOC % ratio has been inadequate since December 2020. Lead & Copper samples required, but missed in 2024. | Take required TOC and TOC/Alkalinity samples, and sample for Lead & Copper | None known
SHARP | No RMW | 99 | KOTZEBUE MUN. WATER SYSTEM / AK2340060 (3234 / C) | [8 empty] | 19 | [14 empty] | They have exceeded the TTHM MCL since 2019 and the HAA5 LRAA since 3rd quarter 2023. | The new ultrafiltration-nanofiltration membrane treatment system began its operation in December 2022, however, the system is still experiencing high DBPs. System needs to optimize their treatment system to reduce the DBP levels. | Monitoring of new WTP will continue throughout the interim operation period (extended to June 2025). DBP precursor removal data is to be analyzed by the design engineering firm to improve DBP results. Elevated manganese levels in winter continue to be an issue. Long term fixes are being designed for implementation this spring and include possibly installing greensand filtration pre-treatment; this may also have an effect on DBP precursor removal. An NF membrane pilot test is to be implemented this winter.
ROBERTS | TCC | 13 | KOYUKUK SAFEWATER FACILITY / AK2360214 (85 / C) | [11 empty] | 8 |  |  |  | 5 | [7 empty] | The system ran out of water in February 2024 due to an inoperable well pump and was placed on a boil water notice. They have not collected a total coliform sample since Jan. 2024 or a distribution chlorine sample since Dec. 2023. | The PWS needs to hire a certified operator to run the water plant and collect all routine compliance samples. | None known
AGUE | YKHC | 24 | KWETHLUK NEW PIPED WATER SYSTEM / AK2272017 (760 / C) | [8 empty] | 4 | [14 empty] | PWS had an HAA5 MCL exceedance in the 3rd quarter of 2024, and failed to meet TOC removal ratios for all of 2024. The exceeding HAA5 sample from July was the last DBP sample collected, and the last TOC/Alkalinity samples were collected in September. | Collect quarterly DBP and monthly TOC/Alkalinity samples and address MCL/TT violations. | None known
BARNES | YKHC | 55 | KWIGILLINGOK WASHETERIA / AK2271700 (400 / C) | [12 empty] | 43 |  |  | 6 |  |  | 2 |  |  |  |  | HAA5 last sampled in 2021. TTHM last taken in 2014. Last LT2 sample taken in 2017. | Operator needs to sample for HAA5 and TTHM, and resume LT2 sampling. Operator needs to develop a Lead & Copper sample plan. | Water tank foundation is unstable; operator cannot fill tank more than halfway.
AGUE | YKHC | 11 | LOWER KALSKAG WATER SYSTEM / AK2270697 (302 / C) | [5 empty] | 1 | [10 empty] | 1 | [6 empty] | System has open significant deficiencies from their 2023 sanitary survey and did not distribute lead consumer notices for samples collected in 2022. | Address open deficiencies and distribute lead consumer notices. | 2023 sanitary survey identified the following deficiencies: improper drainage around the wellhead, potential cross connections created by hanging hoses, and an insufficient air gap at the greensand backwash.
NAKANISHI | YKHC | 17 | NAPASKIAK WEST WATER SYSTEM / AK2260139 (200 / C) | [5 empty] | 2 | [7 empty] | 1 |  | 1 | 1 | [6 empty] | DBPs were due in 2023 and LCR were due in 2023. Significant Deficiencies from 2018 and 2022 surveys with due date of 4/13/2024 remain unresolved. | Collect samples for Lead & Copper and DBP's. Deficiencies from 2022 sanitary survey need to be resolved. For Significant deficiency, follow-up coordination is underway to establish a corrective action plan timeline. | None known
AGUE | YKHC | 12 | NIGHTMUTE NEW WATERING POINT / AK2271721 (243 / C) |  |  |  | 1 |  | 1 | [17 empty] | System had a sanitary survey conducted in 2022, and triggered a Level 1 Assessment in the same year. Both site visits identified similar issues. | Correct significant deficiencies and sanitary defects. | The following hardware issues were identified as sanitary defects or significant deficiencies: no raw water sample tap, issues with drainage around the wellhead, and the watering point hose does not have appropriate backflow prevention and is not made of an NSF-approved material.
NAKANISHI | YKHC | 35 | NUNAM IQUA WATER SYSTEM / AK2270207 (213 / C) | [8 empty] | 5 | [6 empty] | 8 | [7 empty] | Last sampled DBPs, TOC, and alkalinity in 1st quarter 2024. | Sample for TOC and alkalinity from the Intake, and for TOC from the treatment plant monthly, Sample quarterly for DBPs. | None known
DAVIS | DEC | 14 | OLD HARBOR / AK2250061 (246 / C) |  | 1 | [21 empty] | System is not meeting entry point residual disinfection (EPRD) requirements. | Meet EPRD requirements of 0.2 mg/L. | None known
CAHILL | No RMW | 13 | PALMER LIFEWAYS DAYCARE / AK2226055 (56 / NTNC) | [7 empty] | 2 | [6 empty] | 1 | [8 empty] | PWS exceeds Arsenic MCL. | PWS can return to compliance by testing below the Arsenic MCL after receiving approval to operate Arsenic treatment system. | PWS plans to install POU treatment. Engineering submittal request for construction approval has been received and reviewed. Request for clarification and additional information was sent to submitting engineer.
AGUE | No RMW | 11 | PETER PAN SEAFOODS PORT MOLLER / AK2261216 (140 / NC) |  |  |  |  | 1 | [6 empty] | 1 | [11 empty] | Seasonal system did not operate publicly in 2024 and has just been purchased by a new company. System's current treatment configuration does not meet surface water rule requirements. System did not collect a TC sample in August 2023. | Complete engineering process and begin operating filtration system which meets surface water rule requirements. Collect routine TC samples. | Construction of new treatment system was in progress, but was not functioning correctly in 2022. System is in a remote location and is not occupied during the off season.
BARNES | YKHC | 19 | PLATINUM CITY WATER SYSTEM / AK2271059 (51 / C) |  |  |  |  | 1 | [6 empty] | 1 | [6 empty] | 4 | 4 |  |  |  | System does not meet applicable water treatment and filtration requirements. PWS does not have RTCR plan on file. CCR certification forms were not submitted 2016-2022. | Operator needs to develop an RTCR sample siting plan and submit VOC samples. | No filtration or disinfection installed.
HARRIS | DEC | 33 | PORT PROTECTION / AK2121123 (60 / C) | 2 |  |  | 1 | 1 | [18 empty] | Classified as a GWUDISW & has not installed filtration/disinfection. PWS on a long-term BWN due to lack of treatment & repeated TC+/EC+ results. PWS contracted ARWA to perform Level 2 Assessment/Sanitary Survey combo on 1/7/2025. The final report has not yet been submitted for review. | Install filtration & disinfection treatment system. Submit Level 2 Assessment/Sanitary Survey report for review. | Remote system with no electrical grid or financial means to install treatment system. Source water infiltration gallery currently intaking raw water & substrate deposits from creek.
BJORKMAN | No RMW | 21 | SET FREE ALASKA SNODGRASS / AK2220483 (47 / NTNC) | [7 empty] | 4 | [10 empty] | 1 |  |  |  |  | System has had arsenic MCL exceedances since 2022. System classification is under review by DEC, due to reduced population. | System must submit samples under the arsenic MCL (must submit engineering plans for approval prior to any changes to treatment/filtration). | None known
AGUE | YKHC | 14 | SHAGELUK WATER SYSTEM / AK2280040 (60 / C) | [15 empty] | 4 | 5 |  | 1 |  |  |  |  | System last collected complete sets of VOCs in 2019, Lead & Copper in 2021, and DBPs in 2011. | Collect Lead & Copper and VOC samples ASAP. Collect 2 complete sets of DBP samples in July 2025 from appropriate locations. | None known
SHARP | NSHC | 14 | SHAKTOOLIK WATER SYSTEM / AK2340442 (270 / C) | [11 empty] | 1 | 12 |  |  | 1 | [7 empty] | System has not collected a TCR or distribution chlorine violation since September 2024. Has not submitted a completed monthly operator report since February 2024 due to operator turn over. | System must submit completed monthly operator report as soon as possible and collect February 2024 TCR with detectable chlorine residual. | None known
LATIMER | No RMW | 11 | STERLING HARBOR MENNONITE CHURCH / AK2249223 (100 / NC) | [5 empty] | 1 | [7 empty] | 1 | [9 empty] | System has not responded to sanitary survey deficiency letter/call regarding well cap electrical conduit opening compromised, and unapproved modifications with non NSF components. | Correct well cap electrical connection, and address modifications/attain corrective action plan. | Non-NSF components.
HARRIS | DEC | 96 | TATITLEK WATER SYSTEM / AK2291130 (95 / C) | [8 empty] | 18 | [6 empty] | 1 | [6 empty] | 1 | System has ongoing DBP exceedances also exceeding Lead at one location. System will research water storage tank mixer and continue to work with NUS/ANTHC/RMW on updating chlorine injection equipment. | Install treatment to reduce DBP's. Replace faucets where Lead is exceeding. Submit full OEL report to the Department. Complete/distribute HAA5 MCL exceedance public notices to patrons. | High Lead levels in distribution system. The chlorine injection equipment is likely not operating smoothly.
SHARP | TCC | 25 | TOO'GHA INC - IN TANANA / AK2360109 (271 / C) |  | 2 | [10 empty] | 4 |  |  | 1 | [7 empty] | System needs to collect 2025 DBP sample set and submit a completed monthly operator report without turbidity exceedances or inadequate chlorine entry point readings. | System needs to submit completed monthly operator report without turbidity exceedances as soon as possible and adjust treatment accordingly, if needed. System needs to collect June 2025 DBP sample. | None known
AGUE | YKHC | 31 | TUNTUTULIAK WASHETERIA AND WATERING PT / AK2271211 (350 / C) | [5 empty] | 2 |  |  |  | 1 |  |  |  |  | 3 |  | 8 | [6 empty] | System had arsenic exceedances between 2015-2017 and exceeded the action level for lead in 2016. Last samples for both analytes were collected in 2020. PWS has not corrected Significant deficiencies identified in past several sanitary surveys. | Collect arsenic and Lead & Copper samples. Complete Level 1 Assessment and address open significant deficiencies. | System is on a long-term BWN due to inadequate well seal. The following significant deficiencies are unresolved: cross connection between the settling tank overflow and drain, a sewer line is within 100 feet and the sewage lagoon is located within 200 feet of the wellhead, and insufficient drainage around the wellhead.
SHARP | NSHC | 42 | WALES WATER SYSTEM / AK2340191 (173 / C) | [10 empty] | 7 | [5 empty] | 1 |  |  |  | 2 |  |  | System exceeds the RAA MCL for Uranium. System has not collected Uranium sample since 4th quarter 2023. System failed to collect Lead & Copper sample set during 2023 or 2024. | System must continue to collect quarterly Uranium samples and post applicable public notice until the new source can be brought back online and Uranium levels reduce. System must collect 2025 Lead & Copper sample set. | New source and WTP project to address Uranium MCL has been completed, but due to low production from the source, the system had to revert back to using GW well to fill the remainder of the WST for the winter. Requested system collect a uranium sample from the tank to evaluate uranium levels but have not yet received.
KEIM | No RMW | 11 | WILDWOOD HOMES LLC / AK2310853 (114 / C) | [5 empty] | 1 | [10 empty] | 1 | [6 empty] | PWS hasn't completed Lead Consumer Notification for January 2024 Lead/Copper sample set. PWS has an outstanding sanitary survey deficiency for sources of contamination within the protective radius of the well from the 2021 sanitary survey. | PWS must complete Lead Consumer Notification for January 2024 sample set and return certification form to the State. PWS must address all separation distance issues identified. | Separation distance waiver was submitted and reviewed as part of a project to replace water mains/remove private sewer lines (sanitary survey deficiency), but the project has been incomplete since June of 2023. They will also need approval by the Wastewater Program for the project; no wastewater approval request has been received.

## Definitions
DW Program Staff Contact Information
Mat-Su = Office located in Wasilla, AK. Covers the Mat-Su area. Staff: Jamie Bjorkman (Program Coordinator) 262‐3423, Vacant (EPS) 262-8207, Jessica Cahill (EPS) 376-1824, Charity Bare (Engineering Supervisor) 262-3400
Northern = Office located in Fairbanks, AK. Covers the Northern Alaska PWSs. Staff: Teslyn Hakala (Program Coordinator) 451-3038, Michael Sharp (EPS) 451-2178, Jenny Roberts (EPS) 451‐2137, Gretchen Keim (EPS) 451-2231, Johnny Mendez (Engineering Supervisor) 451-5193.
Southcentral / ANC= Office located in Anchorage, AK. Covers Anchorage bowl, Prudhoe Bay, Bethel/YK Delta, Dillingham area, Aleutian Chain, Pribilof and Kodiak Island area PWSs. Staff: Leslie Morrison (Program Coordinator) 269-7619, Elizabeth Nakanishi (EPS) 269‐7517, Kristine Crippen (EPS) 269‐7521, Monica Ague (EPS) 269-7653, John Davis (EPS) 262-8201, Karis Barnes (EPS) 262-8204, Chris Pletnikoff (Engineering Supervisor) 269‐6064.
Kenai / Southeast = Office located in Soldotna, AK. Covers the Kenai Peninsula and Southeast area. Staff: Jamie Bjorkman (Program Coordinator) 262‐3423, James Latimer (EPS) 262-3410, Christina Harris (EPS) 262-3420, Charity Bare (Engineering Supervisor) 262-3400
GENERAL ETT QUESTIONS: Jeanine Vance (EPM) 269-2007, Karen Garland (EPS) 269-7576, Eric Burg (EPS) 262-3401
Link to DW Program Directory (contact information) | http://dec.alaska.gov/eh/dw/contact/
Resource Links
Alaska Community Database Online
The Community Database Online is a portal for information resources about Alaskan Communities and Places of Interest in an interactive format.
Link to Database Online Webpage | https://dcra-cdo-dcced.opendata.arcgis.com/
Alaska Community Photo Library
The Community Photo Library offers a glimpse into Alaska's communities and lifestyle by providing images of places, people, cultural events, public facilities, landscapes, and other dimensions of community life.
Link to Photo Library Webpage | https://www.commerce.alaska.gov/dcra/admin/Photo
Remote Maintenance Worker (RMW) Service Area Abbreviations
BBAHC= Bristol Bay area Health Corporation | Maniilaq= Maniilaq Health Corporation | TCC= Tanana Chiefs Conference
DEC= AK Department of Environmental Conservation | NSHC= Norton Sound Health Corporation | YKHC= Yukon Kuskokwim Health Corporation
No‐RMW= Not served by an RMW Program
Link to RMW Directory | https://dec.alaska.gov/media/p4dntxhf/rmw-directory.pdf
Definitions
AL= Action Level | IFE= Individual Filter Effluent | RMW= Remote Maintenance Worker
ANTHC= Alaska Native Tribal Health Consortium | IOC= Inorganic Chemicals | RTC= Return to compliance (fall off ETT list)
BACTI or t‐Coli = Total Coliform Sample | LCR= Lead/Copper Rule | RTCR= Revised Total Coliform Rule
BWN= Boil Water Notice | LRAA= Locational Running Annual Average (Stage 2) | SOC= Synthetic Organic Chemicals
CCR= Consumer Confidence Report | LT1= Long Term 1 Enhanced Surface Water Treatment Rule | Surface Water (SW)= Surface Water violations Surface Water Treatment Rules (SWTR, LT1, and LT2)
CFE= Combined Filter Effluent | LT2= Long Term 2 Enhanced Surface Water Treatment Rule
DPB= Disinfection by Products | M/R= Monitoring and Reporting (type of violation) | SSUP = Seasonal Startup Procedures
DSRD= Distribution Chlorine Residual | MCL= Maximum Contaminant Level (type of violation) | TC= Total Coliform (also called Bacti)
EHO= Environmental Health Officer | MOR= Monthly operator report | TOC= Total Organic Carbon
EP= Entry Point | NOV= Notice of Violation | TCR= Total Coliform Rule
EPA= Environmental Protection Agency | OCC= Optimal corrosion control (Lead/Copper Rule) | TT= Treatment Technique (violation)
EPRD= Entry Point Residual Distribution | PE= Public Education (requirement under Lead/Copper Rule) | TTHM= Total Trihalomethanes (Stage 1 Rule)
ETT= Enforcement Targeting Tool | PER= Preliminary Engineering Report | VOC= Volatile Organic Chemicals
FANLs= Facility Analyte Level (refers to SW/DBP monitoring requirements) | PN= Public Notice | VSW= Village Safe Water
GAC= Granular Activated Carbon | PWS= Public Water System | WTP= Water Treatment Plant
GWUDI= Groundwater under the direct influence of surface water | RAA= Running Annual Average
HAA5= Haloacetic Acids (Stage 1 Rule) | Rads= Radionuclides Rule