## Cost_Est
|  |  | Rev. 1 | Job No. | 31430.01.00 | Page No. |  | 1
|  |  |  | Subject | Aurora Energy Chena - Dry Sorbent Injection
Computed by | J. Smith / S. Worcester/ D. Bacon | Date | 2019-02-08 |  | Updatded Opinion of Probable Cost
Updated by | J. Solan | Date | 2023-01-22
|  |  |  | Sheet No. | 1 | of |  | 1
Item Description |  |  |  | Quantity |  | Unit Cost (2019) | Unit Cost (2023) | Total Cost | Chem. Eng PCI - 2018 | 603.1
[9 empty] | Chem. Eng PCI - 2022 | 816
|  |  |  | No. of Unit | UOM |  |  |  | Cost Escallation Factor | 135.3%
Engineering Services | [8 empty] | Data Source/Notes
Engineering services provided throughout the project to assist with BOP design, technical specifications, procurement, bid evaluation, and construction observation. |  |  |  | 1 | EA |  | 7483700 | 7483700 | 10% of PROBABLE EQUIPMENT AND CONSTRUCTION COST
Dry Sorbent Injection System Supply
DSI | Includes Railcar offloading, long term storage silos, day storage silos, milling, metering and feed. |  |  | 1 | EA |  | 5990000 | 5990000 | Per Revised BACT Estimate
DSI Installation | Field Installation |  |  | 1 | EA |  | 488847.0691 | 488847.0691 | Escalated from 2019 to 2023
DSI Equipment Freight | DDP jobsite |  |  | 1 | EA |  | 250000 | 250000 | Per Revised BACT Estimate
Baghouse | Includes the baghouse casing itself, cleaning system, support steel, local access, stairtower, local instruments, piping from pulse valves to receiver at grade, and an allowance for field service support, but reusing the plant air system for cleaning |  |  | 1 | EA |  | 2900000 | 2900000 | Per Andritz Email
Baghouse Installation | Field Installation |  |  | 1 | EA |  | 322667.4099 | 322667.4099 | Per Haskell Estimate
Baghouse Freight | DDP jobsite |  |  | 1 | EA |  | 348000 | 348000 | Per Andritz Shipping Email 12% of equipment cost
Demolition
Existing Warehouse |  |  |  | 1 | EA |  | 500000 | 500000
Existing Baghouse and ID Fan Buidling |  |  |  | 1 | EA |  | 500000 | 500000
Structural
Silo Foundation |  |  |  | 2 | EA |  | 186396 | 372792 | Per Haskell Estimate
Sorbent Building Substructure |  |  |  | 1 | EA |  | 183008.8 | 183008.8 | Per Haskell Estimate
Sorbent Building Superstructure |  |  |  | 1 | EA |  | 2754613.1054 | 2754613.1054 | Per Haskell Estimate
Sorbent Building Exterior Closure |  |  |  | 1 | EA |  | 642600 | 642600 | Per Haskell Estimate
Sorbent Building Roofing |  |  |  | 1 | EA |  | 140940 | 140940 | Per Haskell Estimate
Baghouse Substructure |  |  |  | 1 | EA |  | 567933.0957 | 567933.0957 | Per Haskell Estimate
Baghouse Superstructure |  |  |  | 1 | EA |  | 4087081.611 | 4087081.611 | Per Haskell Estimate
Baghouse Exterior Closure |  |  |  | 1 | EA |  | 987425.0341 | 987425.0341 | Per Haskell Estimate
Baghouse Roofing |  |  |  | 1 | EA |  | 437542.6251 | 437542.6251 | Per Haskell Estimate
Railcar Unloading Skid Foundation |  |  |  | 5 | CY | 1500 | 2029.5142 | 10147.5709 | Per Haskell Estimate
Transfer Skid Enclosure Foundation |  |  |  | 5 | CY | 1500 | 2029.5142 | 10147.5709 | Per Haskell Estimate
MCC Foundation |  |  |  | 4 | CY | 1500 | 2029.5142 | 8118.0567 | Per Haskell Estimate
Pipe Bridge by Silos - Steel | coal yard front end loader drive under. |  |  | 4 | TONS | 10800 | 14612.5021 | 58450.0083 | Per Haskell Estimate
Pipe Bridge by Silos - Foundations |  |  |  | 6 | CY | 1250 | 1691.2618 | 10147.5709 | Per Haskell Estimate
Outside Pipe Supports - Steel |  |  |  | 10 | TONS | 10800 | 14612.5021 | 146125.0207 | Per Haskell Estimate
Outside Pipe Supports - Foundations |  |  |  | 40 | CY | 1000 | 1353.0095 | 54120.378 | Per Haskell Estimate
Inside Pipe Supports - Steel |  |  |  | 3 | TONS | 10800 | 14612.5021 | 43837.5062 | Per Haskell Estimate
Ductwork | 600' Feet of Ductwork to accommodate new baghouse and new DSI reactors |  |  | 50 | TONS |  | 27571.655 | 1378582.75 | Per Haskell Estimate. 12.5 tons/100 ft.
Stack | Concrete cylinder with stainless steel flue |  |  | 1 | EA | 958150 | 958150 | 958150 | Per UAF. Not adjusted for inflation
ID Fan Building | 3000 sqft * $500/sqft |  |  | 1 | EA | 1500000 | 1500000 | 1500000 | Per Johnson River $/sqft estimate. Costs reduced due to simplicity of building compared to warehouse.
Warehouse Building | 23,000 sqft * $750/sqft |  |  | 1 | EA | 17250000 | 17250000 | 17250000 | Per Johnson River $/sqft estimate.
Mechanical
Unit 1 Aggregate Piping Cost: 6" Sch 80 Pipe/Fittings/Flanges/Supports - Sorbent Prep to Injection Location |  |  |  | 300 | LF | 350 | 473.5533 | 142065.9924 | Per Haskell Estimate
Unit 2 Aggregate Piping Cost: 6" Sch 80 Pipe/Fittings/Flanges/Supports - Sorbent Prep to Injection Location |  |  |  | 310 | LF | 350 | 473.5533 | 146801.5255 | Per Haskell Estimate
Unit 3 Aggregate Piping Cost: 6" Sch 80 Pipe/Fittings/Flanges/Supports - Sorbent Prep to Injection Location |  |  |  | 280 | LF | 350 | 473.5533 | 132594.9262 | Per Haskell Estimate
Unit 5 Aggregate Piping Cost: 6" Sch 80 Pipe/Flanges/Supports - Sorbent Prep to Injection Location |  |  |  | 200 | LF | 350 | 473.5533 | 94710.6616 | Per Haskell Estimate
Baghouse Ash Piping: 6" Sch 80 |  |  |  | 200 | LF | 350 | 473.5533 | 94710.6616 | Per Haskell Estimate
Electrical
Medium Voltage Switchgear | Mtl & Labor |  |  | 1 | EA |  | 192750 | 192750 | 2023 Vendor Quote + RSMeans Labor
13.8kV to 480V Transformers | Mtl |  |  | 2 | EA |  | 110000 | 220000 | 2023 Vendor Quote
480V MCC | Mtl & Labor |  |  | 2 | EA |  | 103750 | 207500 | 2021 Vendor Quote + RSMeans Labor
480V Panelboard and Xfmr | Mtl & Labor |  |  | 2 | EA |  | 11805 | 23610 | 2021 Vendor Quote + RSMeans Labor
Cable - 15kV, 3 Cond, #2 AWG | Mtl & Labor |  |  | 2500 | LF |  | 35 | 87500 | Vendor Quote
Cable - 480V - MCC, Loads | Mtl & Labor |  |  | 9000 | LF |  | 20 | 180000 | 5600 ft of 3#12, 500 ft of 3#2/0, 800ft of 6#500. Price from Haskell Estimate
Conduit - RGS | Mtl & Labor |  |  | 9300 | LF |  | 30 | 279000 | 2" Average conduit size. Price from Haskell estimate.
Cable Terminations (Mat'l) | 480V Material & Labor |  |  | 496 | EA |  | 100 | 49600 | Per Haskell Estimate
Light Fixtures Interior/Exterior | Surface mounted LED light fixtures (Mtl & Labor) |  |  | 50 | EA |  | 2000 | 100000 | Per Haskell Estimate
Ground Grid extension | Mtl & Labor |  |  | 1050 | LF |  | 15 | 15750 | Per Haskell Estimate
Instrumentation & Controls
BOP DCS Aspects |  |  |  | 1 | EA | 76428 | 103407.8063 | 103407.8063
Heavy Equipment
All Terrain Forklift | 45' lift, 35' reach, 9000 lb. capacity |  |  | 24 | WK |  | 7200 | 172800 | Per Haskell Estimate
Hydraulic Crane | 80-ton |  |  | 135 | DY |  | 4900 | 661500 | Per Haskell Estimate
[6 empty] | Furnish and Erection Subtotal |  | 45805578.7564
[5 empty] | MOBILIZATION / DEMOBILIZATION & MISC COSTS | 5% |  | 2290278.9378 | Per Haskell Estimate |  | 8% | 3664446.3005
[5 empty] | PRIME CONTRACTOR INDIRECT LABOR | 10% |  | 4531687.8756 | Per Haskell Estimate |  | 40% | 15492511.5026
[5 empty] | CONTRACTOR OH & LABOR BURDENS ON PRIME CONTRACTORS LABOR | 15% |  | 6870836.8135 | Per Haskell Estimate |  | 15% | 6870836.8135
[5 empty] | EQUIPMENT & SMALL TOOLS | 5% |  | 2248563.9378 | Per Haskell Estimate |  | 10% | 4514407.8756
[5 empty] | CONTINGENCY | 10% |  | 6174694.6321 | Cost Manual |  | 15% | 11452167.1873
[5 empty] | PROFIT | 10% |  | 6174694.6321 | Per Haskell Estimate |  | 10% | 7634778.1249
[5 empty] | BOND | 1% |  | 740963.3559 | Per Haskell Estimate |  | 2% | 1908694.5312
[6 empty] | Total Construction Cost |  | 74837298.9413 |  |  |  | 97343421.092
[6 empty] | PROBABLE EQUIPMENT & CONSTRUCTION COST |  | 74837000
[6 empty] | PROBABLE ENGINEERING, EQUIPMENT & CONSTRUCTION COST |  | 82321000
Note: All costs presented in this document are Stanley Consultants' opinions of probable project, construction, and/or operation and maintenance costs. This estimate of probable construction cost is based on our experience and represent our best judgment. We have no control over cost of labor, materials, equipment, contractor's methods, or over competitive bidding or market conditions. Therefore, we do not guarantee that proposals, bids, or actual construction costs will not vary from estimates of project costs, construction, and/or operation and maintenance costs presented. The costs identified are based on Means Building Construction Cost Data, Engineering News Record Construction Cost Index, and/or vendor quotes.

## Haskell Cost_Est Detail
|  |  | Rev. 1 | Job No. | 31430.01.00 | Page No. |  | 1
|  |  |  | Subject | Aurora Energy Chena - Dry Sorbent Injection
Computed by | J. Smith / S. Worcester/ D. Bacon | Date | 2019-02-08 |  | Updatded Opinion of Probable Cost
Updated by | J. Solan | Date | 2023-09-07
Approved by |  | Date |  | Sheet No. | 1 | of |  | 1
Item Description |  |  |  | Quantity |  | Unit Cost (2019) | Unit Cost (2023) | Total Cost | Chem. Eng PCI - 2018 | 603.1
[9 empty] | Chem. Eng PCI - 2022 | 816 | Based in 2023 dollars
|  |  |  | No. of Unit | UOM |  |  |  | Cost Escallation Factor | 135.3% | QTY | UOM | HOURS | LABOR DOLLARS | MATERIAL | SUBCONTRACT | TOTAL | NOTES
Engineering Services | [8 empty] | Data Source
Engineering services provided throughout the project to assist with BOP design, technical specifications, procurement, bid evaluation, and construction observation. |  |  |  | 1 | EA |  | 0 | 0 | 10% of PROBABLE EQUIPMENT AND CONSTRUCTION COST | [7 empty] | 0
0
Dry Sorbent Injection System Supply | [16 empty] | 0
DSI | Includes Railcar offloading, long term storage silos, day storage silos, milling, metering and feed. |  |  | 1 | EA |  | 5990000 | 5990000 | Per Revised BACT Estimate | [7 empty] | 0
DSI Installation | Field Installation |  |  | 1 | EA | 1550000 | 2097164.6493 | 2097164.6493 | Escalated from 2019 to 2023 |  | 1 | LS | 5346.5 | 488847.0691 |  |  | 488847.0691 | Includes silo, pump, day bin and and filter receiver installation based on Eielson. Used a current boilermaker journeymen rate ($88.77/hr) x 3% because the wage change happens at the end of September 2023.
DSI Equipment Freight | FOB jobsite |  |  | 1 | EA |  | 250000 | 250000 | Per Revised BACT Estimate | [7 empty] | 0
Baghouse | Includes the baghouse casing itself, cleaning system, support steel, local access, stairtower, local instruments, piping from pulse valves to receiver at grade, and an allowance for field service support, but reusing the plant air system for cleaning |  |  | 1 | EA |  | 2900000 | 2900000 | Per Andritz Email | [7 empty] | 0
Baghouse Installation | Field Installation |  |  | 1 | EA |  | 0 | 0 |  |  | 6 | CELL | 3529 | 322667.4099 |  |  | 322667.4099 | UAF was a six hopper pulse jet fabric filter. Used a current boilermaker journeymen rate ($88.77/hr) x 3% because the wage change happens at the end of September 2023.
Baghouse Freight | DDP jobsite |  |  | 1 | EA |  | 0 | 0 | [8 empty] | 0 | See if the person that gave you the quote can give you the approximate number of loads that need to be shipped.
0
Structural | [16 empty] | 0
Silo Foundation |  |  |  | 2 | EA | 244304 | 330545.621 | 661091.2419 | Escalated from 2019 to 2023 |  | 177.2222 | CY | 1772.2222 | 124268.2222 | 62127.7778 |  | 186396 | Used the SF dimenions of the Eielson sorbent silo foundation. Assumed a thickness of 3'. Includes formwork, rebar and concrete labor and material. Used a laborer rate of $70.12 per hour x 1.03 because the rate expired in June 2023.
Sorbent Building Substructure |  |  |  | 1 | EA | 247047 | 334256.9259 | 334256.9259 | Escalated from 2019 to 2023 |  | 174 | CY | 1740 | 122008.8 | 61000 |  | 183008.8 | Used the floor SF from the Eielson sorbent building and used a thickness of 3'. Includes formwork, rebar and concrete labor and material. Used a laborer rate of $70.12 per hour x 1.03 because the rate expired in June 2023.
Sorbent Building Superstructure |  |  |  | 1 | EA | 183067 | 247691.3812 | 247691.3812 | Escalated from 2019 to 2023 |  | 186.1241 | TN | 2791.8616 | 241379.3255 | 2513233.7799 |  | 2754613.1054 | Ratioed the tons of steel based on the tons of steel per SF for the UAF baghouse building. Used a current ironworker journeymen rate ($83.94/hr) x 3% because the wage change happened in July 2023. Material pricing is based on current price charged for the Healy structure.
Sorbent Building Exterior Closure |  |  |  | 1 | EA | 160334 | 216933.4173 | 216933.4173 | Escalated from 2019 to 2023 |  | 7140 | SF |  |  |  | 642600 | 642600 | Used the height, length and width from the Eielson sorbent building. The subcontract includes material and labor for siding and is based on siding and roofing pricing for our SCR building at Healy.
Sorbent Building Roofing |  |  |  | 1 | EA | 12149 | 16437.7118 | 16437.7118 | Escalated from 2019 to 2023 |  | 1566 | SF |  |  |  | 140940 | 140940 | Used length and width from the Eielson sorbent building. The subcontract includes material and labor for siding and is based on siding and roofing pricing for our SCR building at Healy.
Baghouse Substructure |  |  |  | 1 | EA | 247047 | 334256.9259 | 334256.9259 | Escalated from 2019 to 2023 |  | 540.1761 | CY | 5401.7608 | 378771.4675 | 189161.6281 |  | 567933.0957 | Used the floor SF of the baghouse drawing supplied by Solan and assumed a foundation 3' thick. Includes formwork, rebar and concrete labor and material.
Baghouse Superstructure |  |  |  | 1 | EA | 183067 | 247691.3812 | 247691.3812 | Escalated from 2019 to 2023 |  | 286 | TN | 2605 | 225223.611 | 3861858 |  | 4087081.611 | Used UAF baghouse quantity. Used a current ironworker journeymen rate ($83.94/hr) x 3% because the wage change happened in July 2023. Material pricing is based on current price charged for the Healy structure.
Baghouse Exterior Closure |  |  |  | 1 | EA | 160334 | 216933.4173 | 216933.4173 | Escalated from 2019 to 2023 |  | 10971.3893 | SF |  |  |  | 987425.0341 | 987425.0341 | Quantities are based on baghouse sketch supplied by Solan. 20% was added for additional hieght above and below the baghouse. The subcontract includes material and labor for siding and is based on siding and roofing pricing for our SCR building at Healy.
Baghouse Roofing |  |  |  | 1 | EA | 12149 | 16437.7118 | 16437.7118 | Escalated from 2019 to 2023 |  | 4861.5847 | SF |  |  |  | 437542.6251 | 437542.6251 | Quantities are based on baghouse sketch supplied by Solan. 100% was added for room around the baghouse. The subcontract includes material and labor for siding and is based on siding and roofing pricing for our SCR building at Healy.
Railcar Unloading Skid Foundation |  |  |  | 5 | CY | 1500 | 2029.5142 | 10147.5709 | Haskell 2019 Estimate. Escalated from 2019 to 2023 | [7 empty] | 0 | Orignal estimate in column J still "ok"
Transfer Skid Enclosure Foundation |  |  |  | 5 | CY | 1500 | 2029.5142 | 10147.5709 | Haskell 2019 Estimate. Escalated from 2019 to 2023 | [7 empty] | 0 | Orignal estimate in column J still "ok"
MCC Foundation |  |  |  | 4 | CY | 1500 | 2029.5142 | 8118.0567 | Haskell 2019 Estimate. Escalated from 2019 to 2023 | [7 empty] | 0 | Orignal estimate in column J still "ok"
Pipe Bridge by Silos - Steel | coal yard front end loader drive under. |  |  | 4 | TONS | 10800 | 14612.5021 | 58450.0083 | Haskell 2019 Estimate. Escalated from 2019 to 2023 | [7 empty] | 0 | Orignal estimate in column J still "ok"
Pipe Bridge by Silos - Foundations |  |  |  | 6 | CY | 1250 | 1691.2618 | 10147.5709 | Haskell 2019 Estimate. Escalated from 2019 to 2023 | [7 empty] | 0 | Orignal estimate in column J still "ok"
Outside Pipe Supports - Steel |  |  |  | 10 | TONS | 10800 | 14612.5021 | 146125.0207 | Haskell 2019 Estimate. Escalated from 2019 to 2023 | [7 empty] | 0 | Orignal estimate in column J still "ok"
Outside Pipe Supports - Foundations |  |  |  | 40 | CY | 1000 | 1353.0095 | 54120.378 | Haskell 2019 Estimate. Escalated from 2019 to 2023 | [7 empty] | 0 | Orignal estimate in column J still "ok"
Inside Pipe Supports - Steel |  |  |  | 3 | TONS | 10800 | 14612.5021 | 43837.5062 | Haskell 2019 Estimate. Escalated from 2019 to 2023 | [7 empty] | 0 | Orignal estimate in column J still "ok"
Ductwork | 1000' Feet of Ductwork to accommodate new baghouse |  |  | 50 | TONS | 15000 | 20295.1418 | 1014757.0884 | Haskell 2019 Estimate. Escalated from 2019 to 2023. Confirm ductwork tonage |  | 50 | TN | 2500 | 228582.75 | 1150000 |  | 1378582.75 | Used boilermaker wage rate x 50 hours per ton, which comes from a recently (2023) awarded project. Used $23000 per ton based on a recent quote. This does not include refractory.
0
Mechanical | [16 empty] | 0
Unit 1 Aggregate Piping Cost: 6" Sch 80 Pipe/Fittings/Flanges/Supports - Sorbent Prep to Injection Location |  |  |  | 300 | LF | 350 | 473.5533 | 142065.9924 | Haskell 2019 Estimate. Escalated from 2019 to 2023 | [7 empty] | 0 | Orignal estimate in column J still "ok"
Unit 2 Aggregate Piping Cost: 6" Sch 80 Pipe/Fittings/Flanges/Supports - Sorbent Prep to Injection Location |  |  |  | 310 | LF | 350 | 473.5533 | 146801.5255 | Haskell 2019 Estimate. Escalated from 2019 to 2023 | [7 empty] | 0 | Orignal estimate in column J still "ok"
Unit 3 Aggregate Piping Cost: 6" Sch 80 Pipe/Fittings/Flanges/Supports - Sorbent Prep to Injection Location |  |  |  | 280 | LF | 350 | 473.5533 | 132594.9262 | Haskell 2019 Estimate. Escalated from 2019 to 2023 | [7 empty] | 0 | Orignal estimate in column J still "ok"
Unit 5 Aggregate Piping Cost: 6" Sch 80 Pipe/Flanges/Supports - Sorbent Prep to Injection Location |  |  |  | 200 | LF | 350 | 473.5533 | 94710.6616 | Haskell 2019 Estimate. Escalated from 2019 to 2023 | [7 empty] | 0 | Orignal estimate in column J still "ok"
Baghouse Ash Piping: 6" Sch 80 |  |  |  | 200 | LF | 350 | 473.5533 | 94710.6616 | Haskell 2019 Estimate. Escalated from 2019 to 2023 | [7 empty] | 0 | Orignal estimate in column J still "ok"
0
0
Instrumentation & Controls | [16 empty] | 0
BOP DCS Aspects |  |  |  | 1 | EA | 76428 | 103407.8063 | 103407.8063 | Escalated from 2019 to 2023 | [7 empty] | 0
0
Heavy Equipment | [16 empty] | 0
All Terrain Forklift | 45' lift, 35' reach, 9000 lb. capacity |  |  | 24 | WK |  | 7200 | 172800 | Haskell Estimate | [7 empty] | 0 | Orignal estimate in column J still "ok"
Hydraulic Crane | 80-ton |  |  | 135 | DY |  | 4900 | 661500 | Haskell Estimate | [7 empty] | 0 | Orignal estimate in column J still "ok"
0
[6 empty] | Furnish and Erection Subtotal | [10 empty] | 0
0
[5 empty] | MOBILIZATION / DEMOBILIZATION & MISC COSTS | 5% |  |  | Haskell Estimate | [7 empty] | 0 | Orignal estimate in column J still "ok" | 8% | 0
[5 empty] | PRIME CONTRACTOR INDIRECT LABOR | 10% |  |  | Haskell Estimate | [7 empty] | 0 | Orignal estimate in column J still "ok" | 40% | -2829720
[5 empty] | CONTRACTOR OH & LABOR BURDENS ON PRIME CONTRACTORS LABOR | 15% |  |  | Haskell Estimate | [7 empty] | 0 | Orignal estimate in column J still "ok" | 15% | 0
[5 empty] | EQUIPMENT & SMALL TOOLS | 5% |  |  | Haskell Estimate | [7 empty] | 0 | Orignal estimate in column J still "ok" | 10% | -66150
[5 empty] | CONTINGENCY | 10% |  |  | Cost Manual | [7 empty] | 0 | Orignal estimate in column J still "ok" | 15% | -434380.5
[5 empty] | PROFIT | 10% |  |  | Haskell Estimate | [7 empty] | 0 | Orignal estimate in column J still "ok" | 10% | -289587
[5 empty] | BOND | 1% |  |  | Haskell Estimate | [7 empty] | 0 | Orignal estimate in column J still "ok" | 2% | -72396.75
0
[6 empty] | Total Construction Cost | [10 empty] | 0 |  |  | -3692234.25
0
[6 empty] | PROBABLE EQUIPMENT & CONSTRUCTION COST | [10 empty] | 0
[6 empty] | PROBABLE ENGINEERING, EQUIPMENT & CONSTRUCTION COST | [10 empty] | 0
Note: All costs presented in this document are Stanley Consultants' opinions of probable project, construction, and/or operation and maintenance costs. This estimate of probable construction cost is based on our experience and represent our best judgment. We have no control over cost of labor, materials, equipment, contractor's methods, or over competitive bidding or market conditions. Therefore, we do not guarantee that proposals, bids, or actual construction costs will not vary from estimates of project costs, construction, and/or operation and maintenance costs presented. The costs identified are based on Means Building Construction Cost Data, Engineering News Record Construction Cost Index, and/or vendor quotes.