## Total Capital Investment
[8 empty] | Shaded cells indicate user inputs. | [9 empty] | Shaded cells indicate user inputs.
Total Capital Investment - CDS (Circulating Dry Scrubber) | [7 empty] | Date: | 2022-12-28 | Total Capital Investment - CDS (Circulating Dry Scrubber) | [7 empty] | Date: | 2022-12-28
Project: |  | UAF - BACT Analysis | [5 empty] | Prepared By: | M. Jahn | Project: |  | UAF - BACT Analysis | ADEC Reviewer: Moses Coss |  |  |  |  | Prepared By: | M. Jahn
Vendor: |  | Andritz | [5 empty] | Updated By: | C. Kimball | Vendor: |  | Andritz | [5 empty] | Updated By: | C. Kimball
[8 empty] | Rev: | B | [8 empty] | Rev: | B
Capital Costs | [9 empty] | Capital Costs | [9 empty] | Factor or Quote
DIRECT COSTS |  |  | QTY | UNIT | UNIT COST | TOTAL MATERIALS COST | TOTAL LABOR COST |  |  | DIRECT COSTS |  |  | QTY | UNIT | UNIT COST | % of PEMC | TOTAL LABOR COST
(1) | Purchased equipment and material costs | [8 empty] | (1) | Purchased equipment and material costs
| (a) | Basic equipment | [8 empty] | (a) | Basic equipment
|  | CDS System | 1 | EA | 16950000 | [6 empty] | CDS System | 1 | EA | 16950000 | 82.72%
|  | ID Fan | 1 | EA | 567879 | [6 empty] | ID Fan | 1 | EA | 567879 | 2.771%
|  | Fire System | 1 | EA | 134000 | [6 empty] | Fire System | 1 | EA | 134000 | 0.6539%
|  | HVAC | 1 | EA | 445000 | [6 empty] | HVAC | 1 | EA | 445000 | 2.172%
|  | Demo of existing Water Treatment Building | 1 | EA | 500000 | [6 empty] | Demo of existing Water Treatment Building | 1 | EA | 500000 | 2.44%
|  | Total CDS System | [5 empty] | TOTAL = | 18596879 |  |  | Total CDS System | [5 empty] | TOTAL = | 18596879
| (b) | Instrumentation | [8 empty] | (b) | Instrumentation
|  | Total Instrumentation | 1 | EA | 760000 | [6 empty] | Total Instrumentation | 1 | EA | 760000 | 3.709%
[8 empty] | TOTAL = | 760000 | [8 empty] | TOTAL = | 760000
| (c) | Freight | [8 empty] | (c) | Freight
|  | ID Fan System Freight | 1 | LOT | 112000 | [6 empty] | ID Fan System Freight | 1 | LOT | 112000 | 0.5466% |  |  |  | 19.7225
[8 empty] | TOTAL = | 112000 | [8 empty] | TOTAL = | 112000
| (d) | Extended Outage Costs | [8 empty] | (d) | Extended Outage Costs
|  | Additional days beyond a typical 3 week outage | 21 | days | 48028 | [6 empty] | Additional days beyond a typical 3 week outage | 21 | days | 48028 | 0.2344%
[8 empty] | TOTAL = | 1008588 | [8 empty] | TOTAL = | 1008588
| (e) | Vendor representatives fees | [8 empty] | (e) | Vendor representatives fees
|  | Onsite Vendor Representatives fees (enter no. of days and daily rate) | 7 | Days | 2000 |  |  |  | 14000 |  |  | Onsite Vendor Representatives fees (enter no. of days and daily rate) | 7 | Days | 2000 | 0.00976% |  |  | 14000
[8 empty] | TOTAL = | 14000 | [8 empty] | TOTAL = | 14000
Purchased Equipment and Material Cost (PEMC) | [7 empty] | PEMC = | 20491467 | Purchased Equipment and Material Cost (PEMC) | [7 empty] | PEMC = | 20491467
(2) | Direct Installation Costs | [8 empty] | (2) | Direct Installation Costs
| (a) | Concrete (CDS Building, Duct Supports) | 1 | LOT | 800000 |  |  |  | 800000 |  | (a) | Concrete (CDS Building, Duct Supports) | 1 | LOT | 800000 | 12.24% |  |  | 800000
| (b) | Site Vibro Compaction (CDS Building, Supports) | 1 | LOT | 423000 |  |  |  | 423000 |  | (b) | Site Vibro Compaction (CDS Building, Supports) | 1 | LOT | 423000 | 6.474% |  |  | 423000
| (c) | Structural Steel (CDS Building, Supports, Duct) | 1 | LOT | 3064000 |  |  |  | 3064000 |  | (c) | Structural Steel (CDS Building, Supports, Duct) | 1 | LOT | 3064000 | 46.89% |  |  | 3064000
| (d) | Electrical | 1 | LOT | 883000 |  |  |  | 883000 |  | (d) | Electrical | 1 | LOT | 883000 | 13.51% |  |  | 883000
| (e) | Insulation | 1 | LOT | 66000 |  |  |  | 66000 |  | (e) | Insulation | 1 | LOT | 66000 | 1.01% |  |  | 66000
| (f) | Abovegrade piping | 1 | LOT | 442000 |  |  |  | 442000 |  | (f) | Abovegrade piping | 1 | LOT | 442000 | 6.764% |  |  | 442000
| (g) | Golden Heart Utility Relocation | 1 | LOT | 856212.1586 |  |  |  | 856212.1586 |  | (g) | Golden Heart Utility Relocation | 1 | LOT | 856212.1586 | 13.1% |  |  | 856212.1586
Direct Installation Costs (DIC) - Estimate for new building, foundation, piping, electrical, etc. | [7 empty] | DIC = | 6534212.1586 | Direct Installation Costs (DIC) - Estimate for new building, foundation, piping, electrical, etc. | [5 empty] | 20.1% | of TCI | DIC = | 6534212.1586
[16 empty] | 31.89% | of PEMC
Total Direct Costs (TDC) | [7 empty] | TDC = (PEMC) + (DIC) = | 27025679.1586 | Total Direct Costs (TDC) | [7 empty] | TDC = (PEMC) + (DIC) = | 27025679.1586
INDIRECT COSTS | [9 empty] | INDIRECT COSTS
(3) | Engineering, Procurement & Construction Support Services |  | 10% | % TDC |  |  | 2702567.9159 |  |  | (3) | Engineering, Procurement & Construction Support Services |  | 10% | % TDC |  |  | 2702567.9159
(4) | Performance tests |  | 1 | EA | 75000 |  | 75000 |  |  | (4) | Performance tests |  | 1 | EA | 75000 | 0.366% | 75000
Total Indirect Costs (TIC) | [7 empty] | TIC = | 2777567.9159 | Total Indirect Costs (TIC) | [5 empty] | 204914.67 |  | TIC = | 2777567.9159
MANAGEMENT AND CONTINGENCY COSTS | [9 empty] | MANAGEMENT AND CONTINGENCY COSTS
(5) | Contingency |  | 10% | % TDC |  |  | 2702567.9159 |  |  | (5) | Contingency |  | 10% | % TDC |  |  | 2702567.9159
Total Management and Contingency Costs (TM&CC) | [7 empty] | TM & CC = | 2702567.9159 | Total Management and Contingency Costs (TM&CC) | [7 empty] | TM & CC = | 2702567.9159
TOTAL CAPITAL INVESTMENT (TCI) | [7 empty] | TCI = (TDC)+(TIC)+(TM&CC) = | 32505814.9903 | TOTAL CAPITAL INVESTMENT (TCI) | [7 empty] | TCI = (TDC)+(TIC)+(TM&CC) = | 32505814.9903
|  | Line Number/Description | Title |  | Comment | [6 empty] | Line Number/Description | Title |  | ADEC Comments
|  | Line Number 1a | Total CDS System |  | CDS price provided by OEM Vendor. Cost includes equipment supply and installation costs. Andritz provided a rough installation factor based on material supply. Assumed installation costs were the same as equipment supply. | [6 empty] | Line Number 1a | Total CDS System |  | Cost determined to be reasonable. See comment for TCI below
|  | Line Number 1a | ID Fan |  | Pricing provided by Clarage for new ID Fan. Fan shipping is provided in line number 1c. | [6 empty] | Line Number 1a | ID Fan |  | Cost determined to be reasonable. Quote from Clarage. UAF does not propose the replacement of the existing baghouse, but the ID Fan system upgrade.
|  | Line Number 1a | Fire System |  | Fire System costs for the new CDS Building. Costs were derived from the original UAF estimate and scaled based on a cost/square foot and escalated using CEPCI. | [6 empty] | Line Number 1a | Fire System |  | Cost determined to be reasonable. UAF provided the basis of the cost estimate based on the estimated square footage for a new CDS system building and the individual elements needed for additional fire safety needed as a result of implementing a CDS system.
|  | Line Number 1a | HVAC |  | HVAC costs for the new CDS Building. Costs were derived from the original UAF estimate and scaled based on a cost/square foot and escalated using CEPCI. | [6 empty] | Line Number 1a | HVAC |  | Cost determined to be reasonable. UAF provided the basis of the cost estimate based on the additional heating that will be required for the new building with a square footage of 3,538 SQ FT and estimated $126,069 in 2017 dollars at $35.63/sqft. This value was adjusted to 2021 dollars using the CEPCI index ($44..45/sqft) and a new square footage of 10,000 based on a recommendation by the vendor yielding a total of $445,000. As a point of comparison, in the lower 48 states, capicatl costs for HVAC retrofits for commercial buildings cost $25 to $60 per square foot, so UAF's calculated cost does not seem out of line. EPA's pollution control manual does not have specific guidance on costs associated with hydronic heating.
|  | Line Number 1a | Water Treatment Building Demolition |  | Water Treatment Building Demolition costs to demolish the existing water treatment building. The new CDS building will be built in it's place. Estimated costs were derived on a level of effort basis | [6 empty] | Line Number 1a | Water Treatment Building Demolition |  | Cost determined to be reasonable. UAF provided labor and equipment costs based on CSI costs schedule
|  | Line Number 1b | Total Instrumentation |  | Total costs for new cabinets and integrating CDS I/O into existing UAF DCS. | [6 empty] | Line Number 1b | Total Instrumentation |  | Cost determined to be reasonable. UAF provided estimate based on a project Stanley Consultans, Inc. designed in 2016 in Iowa, with personal and plant costs adjusted to 2021 and to reflect the project to be located in Fairbanks, AK. No equivalent guidance on backup control costs were found in EPA's pollution control manual except that it susggests that typical Instrumentation costs are around 10% of total equipment costs vs th 3.7% estimated by UAF.
|  | Line Number 1c | ID Fan Shipping Costs |  | Costs to ship ID fan to site. | [6 empty] | Line Number 1c | ID Fan Shipping Costs |  | Cost determined to be reasonable. Table 2.4 of EPA's pollution control manual lists a typical value of 0.05% of the total equipment cost as guidance for freight costs. UAF freight cost represent approximately 0.55% of the cost of the ID fan, which is equivalent to EPA's cost guidance.
|  | Line Number 1d | Extended Outage Costs |  | UAF typically schedules for a 3 week outage on Boiler #5. A CDS outage will take 6 weeks and University will incur 3 additional weeks of outage costs that include purchasing electric power and running additional boilers for steam generation. Costs per day were provided by UAF personnel. The daily outage cost calculations are presented in the last section of Appendix G beginning on page G-73. | [6 empty] | Line Number 1d | Extended Outage Costs |  | Cost determined to be reasonable. No equivalent guidance on extended outage costs were found in EPA's pollution control manual.
|  | Line Number 1e | Vendor Representative Costs |  | Costs incurred for OEM to send a Field Technician to the field to confirm installation and provide technical guidance if needed. Cost per day includes hourly burdened rate for employee daily allowances and travel expenses. Based on general engineering and project experience. | [6 empty] | Line Number 1e | Vendor Representative Costs |  | Cost determined to be reasonable. No equivalent guidance on vendor representative costs were found in EPA's pollution control manual.
|  | Line Number 2a thru 2g | Direct Install Costs |  | Costs broken down into individual disciplines for balance of plant equipment, materials and labor for the CDS System. Cost estimate basis for each discipline are provided as attachments. | [6 empty] | Line Number 2a thru 2g | Direct Install Costs |  | Cost determined to be reasonable. UAF calculate the Direct Installation Costs as approximately 20% of the TCI. In section 2.6.1.2, the EPA's pollution control manual provides installation costs for Venturi Scrubbers, listing them as 0.56 of PEC. UAF determined that the installation costs would be be around 0.32 of PECM. An article published by William Vatavuk from the US EPA and Robert Neveril from Gard, Inc published in the Chemical Engineering Journal in November 1980, provides a multiplier for for direct installation costs for gas absorbers of 0.85 of the base price. UAF's estimate is below this value and within 30% of EPA's 1980 article.
|  | Line Number 3 | Engineering Services |  | Costs for Preliminary Engineering costs to assist the University in soliciting bidders with specifications, preliminary drawings and procurement support for the AQCS system. Additional services include home office support for shop drawing review and occasional site support during construction for potential issues. Engineering is a percentage of the Total Direct Costs of the Project. | [6 empty] | Line Number 3 | Engineering Services |  | Cost determined to be reasonable. In section 2.6.1.2, the EPA's pollution control manual provides installation costs for Venturi Scrubbers, listing them as 0.1 of PEC. UAF used the same factor for this line item.
|  | Line Number 4 | Performance Test |  | Costs for a 3rd party performance testing company to validate emissions and performance guarantees by CDS vendor during operation | [6 empty] | Line Number 4 | Performance Test |  | Cost determined to be reasonable. In table 1.2, the EPA's pollution control manual provides performance tests costs as 0.01 of PEC ($200K). That is, UAF's estimate ($75K) is well under EPA's manual.
|  | Line Number 5 | Construction Contingency |  | Construction Contingency is an allottment for additonal or unexpected costs during the project. RS Means defines contingency allowances and ranges between 3-20% depending on what design stage the project is in. A 10% contingency is a project that is in Design Development, wheras a Conceptual Design phase allows for a 20% contingency. A 10% contingency for this cost estimate is considered low as the project is still in a Development phase. | [6 empty] | Line Number 5 | Construction Contingency |  | Cost determined to be reasonable. EPA's manual provides for contingency factors for SNCR applications higher than UAF's estimates.
[12 empty] | TCI | TOTAL CAPITAL INVESTMENT (TCI) |  | Cost determined to be resonable. Absent specific TCI information on CDS retrofits for single stack coal power plants, total cost of CDS system may be reasonable. According to a Power Engineering article from 2011 a CDS installed system for a 600 MW plant is about $250MM. A linear relationship (without taking into account economies of scale) would be equivalent to about $15.6MM (in today's dollars) for a 28MW (approx UAF boiler) power plant. While this cost is about half of UAF's TCI estimation, both a larger and smaller plant will likely need the same number and type of components, where a larger plant will simply need components with higher rated capacity (e.g. a larger absorber, larger bi-product silo, etc). Therefore the cost - size relationship may not be linear but follow an S-shaped curve between the smaller and larger capacities considered. In their estimate, UAF does not propose the replacement of the existing baghouse. No equivalent guidance on overall costs for TCI were found in EPA Pollution control cost manual.
Note on V56: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Cost of CDS system seems reasonable. According to a Power Engineering article from 2011 a CDS installed system for a 600 MW plant is about $250MM. A linear relationship (which of course doesn't take into account economies of scale) yields about $15.6MM (in today's dollars) for a 28MW (approx UAF boiler) power plant

## Cost Effectiveness
Shaded cells indicate user inputs
Total Annualized Costs - CDS (Circulating Dry Scrubber) | [7 empty] | Date: | 2022-12-28 | Total Annualized Costs - CDS (Circulating Dry Scrubber) | [7 empty] | Date: | 2022-12-28
Project: |  | UAF - BACT Analysis | [5 empty] | Prepared By: | M. Jahn | Project: |  | UAF - BACT Analysis | [5 empty] | Prepared By: | M. Jahn
Vendor: |  | Andritz | [5 empty] | Updated By: | C. Kimball | Vendor: |  | Andritz | [5 empty] | Updated By: | C. Kimball
[8 empty] | Rev: | B | [8 empty] | Rev: | B
Annualized Costs | [9 empty] | Annualized Costs
DIRECT ANNUAL COSTS |  |  | QTY | UNIT | UNIT COST | TOTAL MATERIALS COST | TOTAL LABOR COST |  | TOTAL | DIRECT ANNUAL COSTS |  |  | QTY | UNIT | UNIT COST | TOTAL MATERIALS COST | TOTAL LABOR COST |  | TOTAL
(1) | Operating Labor |  | 8864 | MH | 49.09 | Excluded | 435133.76 |  | 435133.76 | (1) | Operating Labor |  | 8864 | MH | 49.09 | Excluded | 435133.76 |  | 435133.76
(2) | Supervisory Labor |  |  | MH |  | Excluded | Excluded |  | Excluded | (2) | Supervisory Labor |  |  | MH |  | Excluded | Excluded |  | Excluded
(3) | Maintenance Labor |  | 520 | MH | 49.09 | Excluded | 25526.8 |  | 25526.8 | (3) | Maintenance Labor |  | 520 | MH | 49.09 | Excluded | 25526.8 |  | 25526.8
(4) | Maintenance Materials |  | 1 | LOT | 25526.8 | 25526.8 | Excluded |  | 25526.8 | (4) | Maintenance Materials |  | 1 | LOT | 25526.8 | 25526.8 | Excluded |  | 25526.8 | 0.4233% | of TAC
(5) | Utilities | [8 empty] | (5) | Utilities
| (a) | Reagent: |  | TON | 0 | N/A | N/A |  | N/A |  | (a) | Reagent: |  | TON | 0 | N/A | N/A |  | N/A
| (b) | Electricity: | 5452399.2 | kWh | 0.205 | 1117741.836 | Excluded |  | 1117741.836 |  | (b) | Electricity: | 5452399.2 | kWh | 0.205 | 1117741.836 | Excluded |  | 1117741.836
| (c) | Water: | 8935.2 | (K) Gallons | 11.3 | 100967.76 | Excluded |  | 100967.76 |  | (c) | Water: | 8935.2 | (K) Gallons | 11.3 | 100967.76 | Excluded |  | 100967.76
Total Direct Annual Costs (TDAC) | [7 empty] | TDAC = | 1704896.956 | Total Direct Annual Costs (TDAC) | [7 empty] | TDAC = | 1704896.956
INDIRECT ANNUAL COSTS | [9 empty] | INDIRECT ANNUAL COSTS
(6) | Overhead |  | 1% | % |  |  | 325058.1499 |  | 325058.1499 | (6) | Overhead |  | 1% | % |  |  | 325058.1499 |  | 325058.1499
(7a) | Administrative Charges, Insurance |  | 3% | % total capital |  |  | 975174.4497 |  | 975174.4497 | (7a) | Administrative Charges, Insurance |  | 3% | % total capital |  |  | 975174.4497 |  | 975174.4497
(7b) | Capital Recovery Factor [see inputs below] |  | 0.084671 | [6 empty] | (7b) | Capital Recovery Factor [see inputs below] |  | 0.093051
(8) | Capital Recovery | [6 empty] | CRF * TCI = | 2752307.5249 | (8) | Capital Recovery | [6 empty] | CRF * TCI = | 3024684.7858
Total Indirect Annual Costs (TIAC) | [7 empty] | TIAC = | 4052540.1245 | Total Indirect Annual Costs (TIAC) | [7 empty] | TIAC = | 4324917.3854
TOTAL ANNUALIZED COSTS (TAC) | [7 empty] | TAC = (TDAC) + (TIAC) = | 5757437.0805 | TOTAL ANNUALIZED COSTS (TAC) | [7 empty] | TAC = (TDAC) + (TIAC) = | 6029814.3414
Cost effectiveness ($/ton) | [6 empty] | TAC/Emission Reduction = |  | 55585.3921 | Cost effectiveness ($/ton) | [6 empty] | TAC/Emission Reduction = |  | 58215.0685
|  | Data Inputs for Capital Recovery Factor: |  |  |  |  | Uncontrolled emissions (tpy) = |  | 129.4728 |  |  | Data Inputs for Capital Recovery Factor: |  |  |  |  | Uncontrolled emissions (tpy) = |  | 129.4728
|  | Annual Interest Rate (EPA OAQPS Control Cost Manual) | 7.5 | % |  |  | controlled emissions (tpy) = |  | 25.8946 |  |  | Annual Interest Rate (EPA OAQPS Control Cost Manual) | 8.5 | % |  |  | controlled emissions (tpy) = |  | 25.8946
|  | Project Life (EPA OAQPS Control Cost Manual) | 30 | years |  |  | Reduction (tpy) = |  | 103.5782 |  |  | Project Life (EPA OAQPS Control Cost Manual) | 30 | years |  |  | Reduction (tpy) = |  | 103.5782
Line Number/Description |  |  | Title |  | Stationary Source Comment |  |  |  |  | Line Number/Description |  |  | Title |  | Stationary Source Comment |  |  |  |  | ADEC Comment
Line Number 1 and 3 |  |  | Operating/Maintenance Labor |  | Provided by UAF. Rate is burdoned rate for level of personnel operating and performing maintenance on this type of equipment. Additional FT operations person is assumed per shift. Four total shifts per week. Quarter FT maintenance persons is assumed for the new CDS system. |  |  |  |  | Line Number 1 and 3 |  |  | Operating/Maintenance Labor |  | Provided by UAF. Rate is burdoned rate for level of personnel operating and performing maintenance on this type of equipment. Additional FT operations person is assumed per shift. Four total shifts per week. Quarter FT maintenance persons is assumed for the new CDS system. |  |  |  |  | Cost determined to be reasonable. No similar operating / maintenance labor costs are listed in EPA's pollution control manual.
Line Number 4 |  |  | Maintenance Material |  | Allotment for maintenance materials. Item is equal to the maintenance labor allotment in line 3. |  |  |  |  | Line Number 4 |  |  | Maintenance Material |  | Allotment for maintenance materials. Item is equal to the maintenance labor allotment in line 3. |  |  |  |  | Cost determined to be reasonable. This costs represents < 0.5% of the TAC and seems to insignificant to warrant additional scrutiny.
Line Number 5a |  |  | Reagent |  | CDS vendor will not require injection of reagent for SO2 reduction. |  |  |  |  | Line Number 5a |  |  | Reagent |  | CDS vendor will not require injection of reagent for SO2 reduction. |  |  |  |  | N/A
Line Number 5b |  |  | Electricity |  | Pricing provided by UAF for published utility rates on campus. Electical consumption rate provided by CDS vendor. Additional consumption by larger ID Fan was also included. |  |  |  |  | Line Number 5b |  |  | Electricity |  | Pricing provided by UAF for published utility rates on campus. Electical consumption rate provided by CDS vendor. Additional consumption by larger ID Fan was also included. |  |  |  |  | Cost determined to be reasonable. Power consumption cost was also calculated.
Line Number 5c |  |  | Water |  | Pricing provided by UAF for published utility rates on campus. Water consumption rate provided by CDS vendor. |  |  |  |  | Line Number 5c |  |  | Water |  | Pricing provided by UAF for published utility rates on campus. Water consumption rate provided by CDS vendor. |  |  |  |  | Cost determined to be reasonable.
Line Number 6 |  |  | Overhead |  | Calculated as percent of Total Capital Investment |  |  |  |  | Line Number 6 |  |  | Overhead |  | Calculated as percent of Total Capital Investment |  |  |  |  | Cost determined to be reasonable. In table 1.7, EPA Pollution control manual lists overhead as 60% of total labor and maintenance materials. UAF's estimate is below this estimate.
Line Number 7a |  |  | Admin Charges, etc |  | Calculated as percent of Total Capital Investment |  |  |  |  | Line Number 7a |  |  | Admin Charges, etc |  | Calculated as percent of Total Capital Investment |  |  |  |  | Cost determined to be reasonable.
Line Number 7b |  |  | Capital Recovery Factor |  | EPA calculated factor using Interest Rate and Project Life Span |  |  |  |  | Line Number 7b |  |  | Capital Recovery Factor |  | EPA calculated factor using Interest Rate and Project Life Span |  |  |  |  | The formula used corresponds to the Eq 4.3 in EPA's pollution control manual
Line Number 8 |  |  | Capital Recovery |  | Capital Recovery Factor times Total Capital Investment. |  |  |  |  | Line Number 8 |  |  | Capital Recovery |  | Capital Recovery Factor times Total Capital Investment. |  |  |  |  | Cost determined to be reasonable.
Annual Interest Rate (EPA OAQPS Control Cost Manual) |  |  | Annual Interest Rate |  | Latest federal prime rate. https://www.federalreserve.gov/releases/h15/ |  |  |  |  | Annual Interest Rate (EPA OAQPS Control Cost Manual) |  |  | Annual Interest Rate |  | Latest federal prime rate. https://www.federalreserve.gov/releases/h15/ |  |  |  |  | Cost determined to be reasonable.
Project Life (EPA OAQPS Control Cost Manual) |  |  | Project Life |  | Project Life expectancy in years. |  |  |  |  | Project Life (EPA OAQPS Control Cost Manual) |  |  | Project Life |  | Project Life expectancy in years. |  |  |  |  | Cost determined to be reasonable.