## Total Capital Investment
Shaded cells indicate user inputs.
Total Capital Investment - CDS (Circulating Dry Scrubber) | [7 empty] | Date: | 2022-12-28
Project: |  | UAF - BACT Analysis | [5 empty] | Prepared By: | M. Jahn
Vendor: |  | Andritz | [5 empty] | Updated By: | C. Kimball
[8 empty] | Rev: | B
Capital Costs
DIRECT COSTS |  |  | QTY | UNIT | UNIT COST | TOTAL MATERIALS COST | TOTAL LABOR COST
(1) | Purchased equipment and material costs
| (a) | Basic equipment
|  | CDS System | 1 | EA | 16950000
|  | ID Fan | 1 | EA | 567879
|  | Fire System | 1 | EA | 134000
|  | HVAC | 1 | EA | 445000
|  | Demo of existing Water Treatment Building | 1 | EA | 500000
|  | Total CDS System | [5 empty] | TOTAL = | 18596879
| (b) | Instrumentation
|  | Total Instrumentation | 1 | EA | 760000
[8 empty] | TOTAL = | 760000
| (c) | Freight
|  | ID Fan System Freight | 1 | LOT | 112000
[8 empty] | TOTAL = | 112000
| (d) | Extended Outage Costs
|  | Additional days beyond a typical 3 week outage | 21 | days | 48028
[8 empty] | TOTAL = | 1008588
| (e) | Vendor representatives fees
|  | Onsite Vendor Representatives fees (enter no. of days and daily rate) | 7 | Days | 2000 |  |  |  | 14000
[8 empty] | TOTAL = | 14000
Purchased Equipment and Material Cost (PEMC) | [7 empty] | PEMC = | 20491467
(2) | Direct Installation Costs
| (a) | Concrete (CDS Building, Duct Supports) | 1 | LOT | 800000 |  |  |  | 800000
| (b) | Site Vibro Compaction (CDS Building, Supports) | 1 | LOT | 423000 |  |  |  | 423000
| (c) | Structural Steel (CDS Building, Supports, Duct) | 1 | LOT | 3064000 |  |  |  | 3064000
| (d) | Electrical | 1 | LOT | 883000 |  |  |  | 883000
| (e) | Insulation | 1 | LOT | 66000 |  |  |  | 66000
| (f) | Abovegrade piping | 1 | LOT | 442000 |  |  |  | 442000
| (g) | Golden Heart Utility Relocation | 1 | LOT | 856212.1586 |  |  |  | 856212.1586
Direct Installation Costs (DIC) - Estimate for new building, foundation, piping, electrical, etc. | [7 empty] | DIC = | 6534212.1586
Total Direct Costs (TDC) | [7 empty] | TDC = (PEMC) + (DIC) = | 27025679.1586
INDIRECT COSTS
(3) | Engineering, Procurement & Construction Support Services |  | 10% | % TDC |  |  | 2702567.9159
(4) | Performance tests |  | 1 | EA | 75000 |  | 75000
Total Indirect Costs (TIC) | [7 empty] | TIC = | 2777567.9159
MANAGEMENT AND CONTINGENCY COSTS
(5) | Contingency |  | 10% | % TDC |  |  | 2702567.9159
Total Management and Contingency Costs (TM&CC) | [7 empty] | TM & CC = | 2702567.9159
TOTAL CAPITAL INVESTMENT (TCI) | [7 empty] | TCI = (TDC)+(TIC)+(TM&CC) = | 32505814.9903
|  | Line Number/Description | Title |  | Comment
|  | Line Number 1a | Total CDS System |  | CDS price provided by OEM Vendor. Cost includes equipment supply and installation costs. Andritz provided a rough installation factor based on material supply. Assumed installation costs were the same as equipment supply.
|  | Line Number 1a | ID Fan |  | Pricing provided by Clarage for new ID Fan. Fan shipping is provided in line number 1c.
|  | Line Number 1a | Fire System |  | Fire System costs for the new CDS Building. Costs were derived from the original UAF estimate and scaled based on a cost/square foot and escalated using CEPCI.
|  | Line Number 1a | HVAC |  | HVAC costs for the new CDS Building. Costs were derived from the original UAF estimate and scaled based on a cost/square foot and escalated using CEPCI.
|  | Line Number 1a | Water Treatment Building Demolition |  | Water Treatment Building Demolition costs to demolish the existing water treatment building. The new CDS building will be built in it's place. Estimated costs were derived on a level of effort basis
|  | Line Number 1b | Total Instrumentation |  | Total costs for new cabinets and integrating CDS I/O into existing UAF DCS.
|  | Line Number 1c | ID Fan Shipping Costs |  | Costs to ship ID fan to site.
|  | Line Number 1d | Extended Outage Costs |  | UAF typically schedules for a 3 week outage on Boiler #5. A CDS outage will take 6 weeks and University will incur 3 additional weeks of outage costs that include purchasing electric power and running additional boilers for steam generation. Costs per day were provided by UAF personnel. The daily outage cost calculations are presented in the last section of Appendix G beginning on page G-73.
|  | Line Number 1e | Vendor Representative Costs |  | Costs incurred for OEM to send a Field Technician to the field to confirm installation and provide technical guidance if needed. Cost per day includes hourly burdened rate for employee daily allowances and travel expenses. Based on general engineering and project experience.
|  | Line Number 2a thru 2g | Direct Install Costs |  | Costs broken down into individual disciplines for balance of plant equipment, materials and labor for the CDS System. Cost estimate basis for each discipline are provided as attachments.
|  | Line Number 3 | Engineering Services |  | Costs for Preliminary Engineering costs to assist the University in soliciting bidders with specifications, preliminary drawings and procurement support for the AQCS system. Additional services include home office support for shop drawing review and occasional site support during construction for potential issues. Engineering is a percentage of the Total Direct Costs of the Project.
|  | Line Number 4 | Performance Test |  | Costs for a 3rd party performance testing company to validate emissions and performance guarantees by CDS vendor during operation
|  | Line Number 5 | Construction Contingency |  | Construction Contingency is an allottment for additonal or unexpected costs during the project. RS Means defines contingency allowances and ranges between 3-20% depending on what design stage the project is in. A 10% contingency is a project that is in Design Development, wheras a Conceptual Design phase allows for a 20% contingency. A 10% contingency for this cost estimate is considered low as the project is still in a Development phase.

## Cost Effectiveness
Shaded cells indicate user inputs
Total Annualized Costs - CDS (Circulating Dry Scrubber) | [7 empty] | Date: | 2022-12-28
Project: |  | UAF - BACT Analysis | [5 empty] | Prepared By: | M. Jahn
Vendor: |  | Andritz | [5 empty] | Updated By: | C. Kimball
[8 empty] | Rev: | B
Annualized Costs
DIRECT ANNUAL COSTS |  |  | QTY | UNIT | UNIT COST | TOTAL MATERIALS COST | TOTAL LABOR COST |  | TOTAL
(1) | Operating Labor |  | 8864 | MH | 49.09 | Excluded | 435133.76 |  | 435133.76
(2) | Supervisory Labor |  |  | MH |  | Excluded | Excluded |  | Excluded
(3) | Maintenance Labor |  | 520 | MH | 49.09 | Excluded | 25526.8 |  | 25526.8
(4) | Maintenance Materials |  | 1 | LOT | 25526.8 | 25526.8 | Excluded |  | 25526.8
(5) | Utilities
| (a) | Reagent: |  | TON | 0 | N/A | N/A |  | N/A
| (b) | Electricity: | 5452399.2 | kWh | 0.205 | 1117741.836 | Excluded |  | 1117741.836
| (c) | Water: | 8935.2 | (K) Gallons | 11.3 | 100967.76 | Excluded |  | 100967.76
Total Direct Annual Costs (TDAC) | [7 empty] | TDAC = | 1704896.956
INDIRECT ANNUAL COSTS
(6) | Overhead |  | 1% | % |  |  | 325058.1499 |  | 325058.1499
(7a) | Administrative Charges, Insurance |  | 3% | % total capital |  |  | 975174.4497 |  | 975174.4497
(7b) | Capital Recovery Factor [see inputs below] |  | 0.084671
(8) | Capital Recovery | [6 empty] | CRF * TCI = | 2752307.5249
Total Indirect Annual Costs (TIAC) | [7 empty] | TIAC = | 4052540.1245
TOTAL ANNUALIZED COSTS (TAC) | [7 empty] | TAC = (TDAC) + (TIAC) = | 5757437.0805
Data Inputs for Capital Recovery Factor:
|  | Annual Interest Rate (EPA OAQPS Control Cost Manual) | 7.5 | %
|  | Project Life (EPA OAQPS Control Cost Manual) | 30 | years
Line Number/Description |  |  | Title |  | Comment
Line Number 1 and 3 |  |  | Operating/Maintenance Labor |  | Provided by UAF. Rate is burdoned rate for level of personnel operating and performing maintenance on this type of equipment. Additional FT operations person is assumed per shift. Four total shifts per week. Quarter FT maintenance persons is assumed for the new CDS system.
Line Number 4 |  |  | Maintenance Material |  | Allotment for maintenance materials. Item is equal to the maintenance labor allotment in line 3.
Line Number 5a |  |  | Reagent |  | CDS vendor will not require injection of reagent for SO2 reduction.
Line Number 5b |  |  | Electricity |  | Pricing provided by UAF for published utility rates on campus. Electical consumption rate provided by CDS vendor. Additional consumption by larger ID Fan was also included.
Line Number 5c |  |  | Water |  | Pricing provided by UAF for published utility rates on campus. Water consumption rate provided by CDS vendor.
Line Number 6 |  |  | Overhead |  | Calculated as percent of Total Capital Investment
Line Number 7a |  |  | Admin Charges, etc |  | Calculated as percent of Total Capital Investment
Line Number 7b |  |  | Capital Recovery Factor |  | EPA calculated factor using Interest Rate and Project Life Span
Line Number 8 |  |  | Capital Recovery |  | Capital Recovery Factor times Total Capital Investment.
Annual Interest Rate (EPA OAQPS Control Cost Manual) |  |  | Annual Interest Rate |  | Latest federal prime rate. https://www.federalreserve.gov/releases/h15/
Project Life (EPA OAQPS Control Cost Manual) |  |  | Project Life |  | Project Life expectancy in years.