## 2011 ST at Chena Power Plant
Statistical Analysis From 2011 Source Test at the Chena Power Plan
(Prepared by Moses Coss, ADEC) |  |  |  | Prepared on: | 2024-02-23
Source Test Date: | 2011-11-19
Emission Units: | Combined Boiler (Chena 1, 2, 3 and 5) Baghouse Stack |  |  |  |  | Calculating Confidence Interval:
Source of individual source test Run info:
Aurora's Source Test Report (pg 40 of PDF doc)
| Run No | Units
Run 1 | 0.0211 | lb/MMBtu
Run 2 | 0.0217 | lb/MMBtu
Run 3 | 0.0388 | lb/MMBtu
Calculation of Standard Deviation: | [5 empty] | At a confidence level of 95%:
| Run No | Units | Xi - mu | (Xi - mu)^2 |  | Since sample size is small, we use the t distribution for a 2 tailed test. For 95% confidence and df = n-1 =2, t=4.303
Run 1 | 0.0211 | lb/MMBtu | -0.0061 | 3.721e-05 |  | t | 4.303
Run 2 | 0.0217 | lb/MMBtu | -0.0055 | 3.025e-05 |  | t*s/SQRT(n): | 0.020387
Run 3 | 0.0388 | lb/MMBtu | 0.0116 | 0.00013456
|  |  | Sum: | 0.00020202 |  | Lower Interval: | 0.0068133 | lb/MMBtu
[6 empty] | Upper Interval: | 0.047587 | lb/MMBtu
No of values (N): | 3
Population Avg: | 0.0272 | lb/MMBtu
Std Dev (sigma) | 0.0082061 | (sample size less than 30)

## 2010 ST at UAF
Summary of 2010 Source Test on Boiler 1 - UAF
Source Test Date: | 11/2-4/2010
Emission Units: | Boiler 1
Source of individual source test Run info:
Alaska Source Testing, January 19, 2011 Report
| Run No | Units | Coal ton/hr | lb/MMBtu
Run 1 | 2.75 | lb/hr | 5.09 | 0.035732
Run 2 | 2.53 | lb/hr | 4.92 | 0.03401
BTU content: | 7560 | btu/lb
Average: |  |  |  | 0.034871